## Figure_latex
(Figure #)
Matlab # | NYAM Gen ID | Engine Type | NYAM Region | Maximum Capacity | Minimum Generation | Startup Notification | Minimum Run Time |  | Minimum Down Time |  | Ramp Rate
[7 empty] | DAM | RTC | DAM | RTC | DAM | RTC
|  |  |  | (MW) | (MW) | (Hrs) | (Hrs) | (5min) | (Hrs) | (5min) | (MW/Hr) | (MW/5min)
1 | 11 | Ont. Import | Upstate | [11 empty] | RTD counter
2 | 15 | Nuke | Upstate | 3500 | 2625 | 48 | 24 | 288 | 24 | 288 | 4 | 0.33333 | 1 | 1 | 14
3 | 2 | Nuke | LHV | 1100 | 825 | 36 | 24 | 288 | 24 | 288 | 4 | 0.33333 | 2 | 2 | 13
4 | 8 | Nuke | LHV | 1100 | 825 | 24 | 24 | 288 | 24 | 288 | 4 | 0.33333 | 3 | 3 | 12
5 | 13 | Steam | Upstate | 1400 | 210 | 18 | 18 | 216 | 18 | 216 | 210 | 19.25 | 4 | 4 | 11
6 | 12 | Steam | Upstate | 1400 | 210 | 12 | 18 | 216 | 18 | 216 | 210 | 19.25 | 5 | 5 | 10
7 | 1 | Steam | LHV | 2900 | 435 | 10 | 14 | 168 | 14 | 168 | 435 | 39.875 | 6 | 6 | 9
8 | 4 | Steam | NYC | 3900 | 585 | 10 | 14 | 168 | 14 | 168 | 585 | 53.625 | 7 | 7 | 8
9 | 6 | Steam | LI | 2600 | 390 | 10 | 14 | 168 | 14 | 168 | 390 | 35.75 | 8 | 8 | 7
10 | 9 | NE Import | ISONE | [7 empty] | 0 |  | 9 | 9 | 6 | -63.25
11 | 16 | CC | Upstate | 5300 | 530 | 2 | 5 | 60 | 4 | 48 | 530 | 48.5833 | 10 | 10 | 5 | 462.75
12 | 5 | CC | NYC | 3300 | 330 | 2 | 4 | 48 | 3 | 36 | 330 | 30.25 | 11 | 11 | 4 | 511.3333 | 529
13 | 3 | GT | NYC | 2600 | 65 | 10 min | 1 | 1 | 1 | 1 | 5000 | 416.6667 | 12 | 12 | 3 | 530 | 577.5833
14 | 7 | GT | LI | 2377 | 59.425 | 10 min | 1 | 1 | 1 | 1 | 5000 | 416.6667 | 13 | 13 | 2
15 | 14 | HQ Import | Upstate | [9 empty] | 14 | 14 | 1
16 | 10 | Ref Bus | Upstate
Max2Min
|  |  |  | Steam | 0.15
|  |  |  | CC | 0.1
|  |  |  | GT | 0.025 |  |  |  |  | Steam and Combined Cycle Ramp Factors
[10 empty] | DAM ramp factor | Multiply original mpc.gen ramp rates by this value to obtain the DAM ramp rates
[10 empty] | RTC ramp factor | Multiply original mpc.gen ramp rates by this value to obtain the RTC ramp rates
[10 empty] | RTD ramp factor | Multiply original mpc.gen ramp rates by this value to obtain the RTD ramp rates

## Figure
(Figure #)
Matlab # | Gen ID | Engine Type | NYAM Region | NYAM Bus # | Maximum Capacity | Minimum Generation | Startup Notification | Minimum Run Time |  | Minimum Down Time |  | Ramp Rate |  | Ramp Rate |  | Ramp Rate
[8 empty] | DAM | RTC | DAM | RTC | DAM |  | RTC |  | RTD
[5 empty] | (MW) | (MW) | (Hrs) | (Hrs) | (5min) | (Hrs) | (5min) | MW/30min | MW/hr | MW/30min | MW/5min | MW/30min | MW/5min
1 | 11 | Reserved | Upstate | [16 empty] | RTD counter
2 | 15 | Nuke | Upstate | 67 | 3500 | 2625 | 48 | 24 | NA | 24 | NA | 2 | 4 | 2 | 0.33333 | 2 | 0.33333 | 1 | 1 | 14
3 | 2 | Nuke | LHV | 54 | 1100 | 825 | 36 | 24 | NA | 24 | NA | 2 | 4 | 2 | 0.33333 | 2 | 0.33333 | 2 | 2 | 13
4 | 8 | Nuke | LHV | 60 | 1100 | 825 | 24 | 24 | NA | 24 | NA | 2 | 4 | 2 | 0.33333 | 2 | 0.33333 | 3 | 3 | 12
5 | 13 | Steam | Upstate | 65 | 1400 | 210 | 18 | 18 | NA | 18 | NA | 105 | 210 | 115.5 | 19.25 | 115.5 | 19.25 | 4 | 4 | 11
6 | 12 | Steam | Upstate | 64 | 1400 | 210 | 12 | 18 | NA | 18 | NA | 105 | 210 | 115.5 | 19.25 | 115.5 | 19.25 | 5 | 5 | 10
7 | 1 | Steam | LHV | 53 | 2900 | 435 | 10 | 14 | NA | 14 | NA | 217.5 | 435 | 239.25 | 39.875 | 239.25 | 39.875 | 6 | 6 | 9
8 | 4 | Steam | NYC | 56 | 3900 | 585 | 10 | 14 | NA | 14 | NA | 292.5 | 585 | 321.75 | 53.625 | 321.75 | 53.625 | 7 | 7 | 8
9 | 6 | Steam | LI | 58 | 2600 | 390 | 10 | 14 | NA | 14 | NA | 195 | 390 | 214.5 | 35.75 | 214.5 | 35.75 | 8 | 8 | 7
10 | 9 | NE Import | ISONE | 61 | 2000 | 0 | [5 empty] | 0 | 0 | 0 |  | 0 |  | 9 | 9 | 6 | -63.25
11 | 16 | CC | Upstate | 68 | 5300 | 530 | 2 | 5 | NA | 2 | NA | 265 | 530 | 291.5 | 48.5833 | 291.5 | 48.5833 | 10 | 10 | 5 | 462.75
12 | 5 | CC | NYC | 57 | 3300 | 330 | 2 | 4 | NA | 2 | NA | 165 | 330 | 181.5 | 30.25 | 181.5 | 30.25 | 11 | 11 | 4 | 511.3333 | 529
13 | 3 | GT | NYC | 55 | 2600 | 65 | 5 min | 1 | 30min | 1 | 30min | 2500 | 5000 | 2500 | 416.6667 | 2500 | 416.6667 | 12 | 12 | 3 | 530 | 577.5833
14 | 7 | GT | LI | 59 | 2377 | 59.425 | 5 min | 1 | 30min | 1 | 30min | 2500 | 5000 | 2500 | 416.6667 | 2500 | 416.6667 | 13 | 13 | 2
15 | 14 | HQ Import | Upstate | 66 | 10000 | 0 | [11 empty] | 14 | 14 | 1
16 | 10 | Ref Bus | Upstate | 62
Max2Min
[5 empty] | Steam | 0.15 |  | wrong…. Old numbers
[5 empty] | CC | 0.1
[5 empty] | GT | 0.025 |  |  |  |  | Steam and Combined Cycle Ramp Factors
[11 empty] | DAM ramp factor | 1 | Multiply original mpc.gen ramp rates by this value to obtain the DAM ramp rates
[11 empty] | RTC ramp factor | 1.1 | Multiply original mpc.gen ramp rates by this value to obtain the RTC ramp rates
[11 empty] | RTD ramp factor | 1.1 | Multiply original mpc.gen ramp rates by this value to obtain the RTD ramp rates
Put these into the matlab simulation variables section on top of Main File

## xgd_uc
Type | Region | Gen Stack Order
|  |  | Bus # | InitialState | CommitKey | CommitSched | MinUp | MinDown | ; | Comments
2016 ITM ICAP | A2F |  | 63
Nuke | A2F | 1 | 67 | -25 | 1 | 1 | 24 | 22 | ; | %1
Nuke | GHI | 2 | 54 | -25 | 1 | 1 | 24 | 22 | ; | %2
Nuke | GHI | 3 | 60 | -25 | 1 | 1 | 24 | 22 | ; | %3
Steam | A2F | 4 | 65 | -25 | 1 | 1 | 18 | 16 | ; | %4
Steam | A2F | 5 | 64 | -25 | 1 | 1 | 18 | 16 | ; | %5
Steam | GHI | 6 | 53 | -25 | 1 | 1 | 14 | 12 | ; | %6
Steam | NYC | 7 | 56 | -25 | 1 | 1 | 14 | 12 | ; | %7
Steam | LI | 8 | 58 | -25 | 1 | 1 | 14 | 12 | ; | %8
NE Import | ISONE | 9 | 61 | -100 | 1 | 1 | 2 | 1 | ; | %9
CC | A2F | 10 | 68 | -25 | 1 | 1 | 5 | 4 | ; | %10
CC | NYC | 11 | 57 | -25 | 1 | 1 | 4 | 3 | ; | %11
GT | NYC | 12 | 55 | -1 | 1 | 1 | 1 | 1 | ; | %12
GT | LI | 13 | 59 | -1 | 1 | 1 | 1 | 1 | ; | %13
HQ Import | A2F | 14 | 66 | -25 | 1 | 1 | 3 | 2 | ; | %14
Ref Bus | A2F |  | 62
*Same for both DAM and RTC

## mpc.gen
Type | Region | Gen Stack Order | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 |  |  |  | 5min ramp limit
|  |  | Bus # | Pg | Qg | Qmax | Qmin | Vg | Mbase | GenStatus | Pmax | Pmin | PC1 | PC2 | QC1MIN | QC1MAX | QC2MIN | QC2MAX | RAMP_AGC | RAMP_10 | RAMP_30 | RAMP_Q | APF | ; | comments | comments | (each unit) | (all units)
2016 ITM ICAP | A2F |  | 1: 63; 2: 0; 3: 0; 4: 999; 5: -999; 6: 1; 7: 100; 8: 1; 9: 7300
Nuke | A2F | 1 | 67 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 3500 | 2625 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.67 | 2 | 0 | 0 | ; | % | Nuke A2F 1 | 0.1 | 0.1
Nuke | GHI | 2 | 54 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 1100 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.67 | 2 | 0 | 0 | ; | % | Nuke GHI 2 |  | 0.1 | 0.1
Nuke | GHI | 3 | 60 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 1100 | 825 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.67 | 2 | 0 | 0 | ; | % | Nuke GHI 3 |  | 0.1 | 0.1
Steam | A2F | 4 | 65 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 1400 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 155.56 | 105 | 0 | 0 | ; | % | Steam A2F 4 |  | 10 | 20
Steam | A2F | 5 | 64 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 1400 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 1.56 | 155.56 | 105 | 0 | 0 | ; | % | Steam A2F 5 |  | 10 | 20
Steam | GHI | 6 | 53 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 2900 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | 3.22 | 322.22 | 217.5 | 0 | 0 | ; | % | Steam GHI 6 |  | 10 | 10
Steam | NYC | 7 | 56 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 3900 | 585 | 0 | 0 | 0 | 0 | 0 | 0 | 4.33 | 433.33 | 292.5 | 0 | 0 | ; | % | Steam NYC 7 |  | 10 | 40
Steam | LI | 8 | 58 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 2600 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 2.89 | 288.89 | 195 | 0 | 0 | ; | % | Steam LI 8 |  | 10 | 10
NE Import | ISONE | 9 | 61 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 83.33 | 0 | 0 | 0 | ; | % | NE Import ISONE 9 |  | 50 | 50
CC | A2F | 10 | 68 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 5300 | 530 | 0 | 0 | 0 | 0 | 0 | 0 | 14.13 | 1413.33 | 265 | 0 | 0 | ; | % | CC A2F 10 |  | 25 | 75
CC | NYC | 11 | 57 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 3300 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 8.8 | 880 | 165 | 0 | 0 | ; | % | CC NYC 11 |  | 25 | 100
GT | NYC | 12 | 55 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 2600 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 17.33 | 1733.33 | 2500 | 0 | 0 | ; | % | GT NYC 12 |  | 25 | 250
GT | LI | 13 | 59 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 2377 | 59.425 | 0 | 0 | 0 | 0 | 0 | 0 | 15.85 | 1584.67 | 2500 | 0 | 0 | ; | % | GT LI 13 | 25 | 250
HQ Import | A2F | 14 | 66 | 0 | 0 | 9999 | -9999 | 1 | 100 | 1 | 10000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83 | 83.33 | 0 | 0 | 0 | ; | % | HQ Import A2F 14 | 50 | 50
Ref Bus | A2F |  | 1: 62
[20 empty] | Orig Steam Ramp Rates | 120% New Rates
[20 empty] | 105 | 126
[20 empty] | 105 | 126
[20 empty] | 217.5 | 261
[20 empty] | 292.5 | 351
[20 empty] | 195 | 234

## mpc.gencost
Type | Region | Gen Stack Order
Bus #
2016 ITM ICAP | A2F |  | 63 | Model | Startup | shutdown | ncost | c2 | c1 | c0 | ;
Nuke | A2F | 1 | 67 | 2 | 80000 | 0 | 3 | 0.001 | 5 | 225 | ;
Nuke | GHI | 2 | 54 | 2 | 80000 | 0 | 3 | 0.001 | 6 | 200 | ;
Nuke | GHI | 3 | 60 | 2 | 80000 | 0 | 3 | 0.001 | 5.5 | 300 | ;
Steam | A2F | 4 | 65 | 2 | 60000 | 0 | 3 | 0.0005 | 9 | 250 | ;
Steam | A2F | 5 | 64 | 2 | 60000 | 0 | 3 | 0.001 | 9 | 300 | ;
Steam | GHI | 6 | 53 | 2 | 60000 | 0 | 3 | 0.001 | 7.5 | 250 | ;
Steam | NYC | 7 | 56 | 2 | 60000 | 0 | 3 | 0.001 | 9 | 175 | ;
Steam | LI | 8 | 58 | 2 | 60000 | 0 | 3 | 0.001 | 8 | 225 | ;
NE Import | ISONE | 9 | 61 | 2 | 300000000 | 0 | 3 | 0.001 | 10 | 808.633 | ;
CC | A2F | 10 | 68 | 2 | 15000 | 0 | 3 | 0.001 | 9.5 | 400 | ;
CC | NYC | 11 | 57 | 2 | 20000 | 0 | 3 | 0.001 | 10 | 350 | ;
GT | NYC | 12 | 55 | 2 | 1000 | 0 | 3 | 0.001 | 13 | 50 | ;
GT | LI | 13 | 59 | 2 | 1000 | 0 | 3 | 0.001 | 13.2 | 50 | ;
HQ Import | A2F | 14 | 66 | 2 | 300000000 | 0 | 3 | 0.001 | 1.0383 | 808.633 | ;
Ref Bus | A2F |  | 62

## mpc.bus
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
Bus No | Bus Type | Pd | Qd | Gs | Bs | Area # | Vm | Va | Base kV | Zone | MaxVm | MinVm | ; | comments
1 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
2 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
3 | 1 | 177.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
4 | 1 | 177.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
5 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
6 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
7 | 1 | 177.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
8 | 1 | 177.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
9 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
10 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
11 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
12 | 1 | 410.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
13 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
14 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
15 | 1 | 410.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
16 | 1 | 410.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
17 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
18 | 1 | 410.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
19 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
20 | 1 | 410.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
21 | 1 | 328.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
22 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
23 | 1 | 328.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
24 | 1 | 328.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
25 | 1 | 177.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
26 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
27 | 1 | 410.4 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
28 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
29 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
30 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
31 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
32 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
33 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
34 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
35 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
36 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
37 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
38 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
39 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
40 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
41 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
42 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
43 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
44 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
45 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
46 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
47 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
48 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
49 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
50 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
51 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
52 | 1 | 189.1 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ;
53 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %1
54 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %2
55 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %3
56 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %4
57 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %5
58 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %6
59 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %7
60 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %8
61 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %9
62 | 3 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %Reference Bus
63 | 1 | 189 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %This is the A2F 2016 ITM Gen Bus. Treat as load for now | 2 | 0 0 0 | 0 | 1 1 | 0 | 100 | 1 | 1.1 | 0.9 | ;
64 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %10
65 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %11
66 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %12
67 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %13
68 | 2 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 230 | 1 | 1.1 | 0.9 | ; | %14

## mpc.branch
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
F_BUS | T_BUS | BR_R | BR_X | BR_B | RATE_A | RATE_B | RATE_C | TAP | SHIFT | BR_STATUS | ANGMIN | ANGMAX | ; | comments
1 | 2 | 0.0035 | 0.0411 | 0.6987 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
1 | 30 | 0.0008 | 0.0074 | 0.48 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
2 | 3 | 0.0013 | 0.0151 | 0.2572 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
2 | 25 | 0.007 | 0.0086 | 0.146 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
2 | 53 | 0 | 0.0181 | 0 | 0 | 0 | 0 | 1.025 | 0 | 1 | -720 | 720 | ;
3 | 4 | 0.0013 | 0.0213 | 0.2214 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
3 | 18 | 0.0011 | 0.0133 | 0.2138 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
4 | 5 | 0.0008 | 0.0128 | 0.1342 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
4 | 14 | 0.0008 | 0.0129 | 0.1382 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
5 | 6 | 0.0002 | 0.0026 | 0.0434 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
5 | 8 | 0.0008 | 0.0112 | 0.1476 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
6 | 7 | 0.0006 | 0.0092 | 0.113 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
6 | 11 | 0.0007 | 0.0082 | 0.1389 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
6 | 54 | 0 | 0.025 | 0 | 0 | 0 | 0 | 1.07 | 0 | 1 | -720 | 720 | ;
7 | 8 | 0.0004 | 0.0046 | 0.078 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
8 | 9 | 0.0023 | 0.0363 | 0.3804 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
9 | 30 | 0.0019 | 0.0183 | 0.29 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
10 | 11 | 0.0004 | 0.0043 | 0.0729 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
10 | 13 | 0.0004 | 0.0043 | 0.0729 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
10 | 55 | 0 | 0.02 | 0 | 0 | 0 | 0 | 1.07 | 0 | 1 | -720 | 720 | ;
12 | 11 | 0.0016 | 0.0435 | 0 | 0 | 0 | 0 | 1.06 | 0 | 1 | -720 | 720 | ;
12 | 13 | 0.0016 | 0.0435 | 0 | 0 | 0 | 0 | 1.06 | 0 | 1 | -720 | 720 | ;
13 | 14 | 0.0009 | 0.0101 | 0.1723 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
14 | 15 | 0.0018 | 0.0217 | 0.366 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
15 | 16 | 0.0009 | 0.0094 | 0.171 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
16 | 17 | 0.0007 | 0.0089 | 0.1342 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
16 | 19 | 0.0016 | 0.0195 | 0.304 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
16 | 21 | 0.0008 | 0.0135 | 0.2548 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
16 | 24 | 0.0003 | 0.0059 | 0.068 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
17 | 18 | 0.0007 | 0.0082 | 0.1319 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
17 | 27 | 0.0013 | 0.0173 | 0.3216 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
19 | 20 | 0.0007 | 0.0138 | 0 | 0 | 0 | 0 | 1.06 | 0 | 1 | -720 | 720 | ;
19 | 56 | 0.0007 | 0.0142 | 0 | 0 | 0 | 0 | 1.07 | 0 | 1 | -720 | 720 | ;
20 | 57 | 0.0009 | 0.018 | 0 | 0 | 0 | 0 | 1.009 | 0 | 1 | -720 | 720 | ;
21 | 22 | 0.0008 | 0.014 | 0.2565 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
22 | 23 | 0.0006 | 0.0096 | 0.1846 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
22 | 58 | 0 | 0.0143 | 0 | 0 | 0 | 0 | 1.025 | 0 | 1 | -720 | 720 | ;
23 | 24 | 0.0022 | 0.035 | 0.361 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
23 | 59 | 0.0005 | 0.0272 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
25 | 26 | 0.0032 | 0.0323 | 0.531 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
25 | 60 | 0.0006 | 0.0232 | 0 | 0 | 0 | 0 | 1.025 | 0 | 1 | -720 | 720 | ;
26 | 27 | 0.0014 | 0.0147 | 0.2396 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
26 | 28 | 0.0043 | 0.0474 | 0.7802 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
26 | 29 | 0.0057 | 0.0625 | 1.029 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
28 | 29 | 0.0014 | 0.0151 | 0.249 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
29 | 61 | 0.0008 | 0.0156 | 0 | 0 | 0 | 0 | 1.025 | 0 | 1 | -720 | 720 | ;
9 | 30 | 0.0019 | 0.0183 | 0.29 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
9 | 36 | 0.0022 | 0.0196 | 0.34 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
9 | 36 | 0.0022 | 0.0196 | 0.34 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
36 | 37 | 0.0005 | 0.0045 | 0.32 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
34 | 36 | 0.0033 | 0.0111 | 1.45 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
35 | 34 | 0.0001 | 0.0074 | 0 | 0 | 0 | 0 | 0.946 | 0 | 1 | -720 | 720 | ;
33 | 34 | 0.0011 | 0.0157 | 0.202 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
32 | 33 | 0.0008 | 0.0099 | 0.168 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
30 | 31 | 0.0013 | 0.0187 | 0.333 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
30 | 32 | 0.0024 | 0.0288 | 0.488 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
1 | 31 | 0.0016 | 0.0163 | 0.25 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
31 | 38 | 0.0011 | 0.0147 | 0.247 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
33 | 38 | 0.0036 | 0.0444 | 0.693 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
38 | 46 | 0.0022 | 0.0284 | 0.43 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
46 | 49 | 0.0018 | 0.0274 | 0.27 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
1 | 47 | 0.0013 | 0.0188 | 1.31 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
47 | 48 | 0.0025 | 0.0268 | 0.4 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
47 | 48 | 0.0025 | 0.0268 | 0.4 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
48 | 40 | 0.002 | 0.022 | 1.28 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
35 | 45 | 0.0007 | 0.0175 | 1.39 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
37 | 43 | 0.0005 | 0.0276 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
43 | 44 | 0.0001 | 0.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
44 | 45 | 0.0025 | 0.073 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
39 | 44 | 0 | 0.0411 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
39 | 45 | 0 | 0.0839 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
45 | 51 | 0.0004 | 0.0105 | 0.72 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
50 | 52 | 0.0012 | 0.0288 | 2.06 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
50 | 51 | 0.0009 | 0.0221 | 1.62 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
49 | 52 | 0.0076 | 0.1141 | 1.16 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
52 | 42 | 0.004 | 0.06 | 2.25 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
42 | 41 | 0.004 | 0.06 | 2.25 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
41 | 40 | 0.006 | 0.084 | 3.15 | 0 | 0 | 0 | 0 | 0 | 1 | -720 | 720 | ;
31 | 62 | 0 | 0.026 | 0 | 0 | 0 | 0 | 1.04 | 0 | 1 | -720 | 720 | ;
32 | 63 | 0 | 0.013 | 0 | 0 | 0 | 0 | 1.04 | 0 | 1 | -720 | 720 | ;
36 | 64 | 0 | 0.0075 | 0 | 0 | 0 | 0 | 1.04 | 0 | 1 | -720 | 720 | ;
37 | 65 | 0 | 0.0033 | 0 | 0 | 0 | 0 | 1.04 | 0 | 1 | -720 | 720 | ;
41 | 66 | 0 | 0.0015 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | -720 | 720 | ;
42 | 67 | 0 | 0.0015 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | -720 | 720 | ;
52 | 68 | 0 | 0.003 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | -720 | 720 | ;
1 | 27 | 0.032 | 0.32 | 0.41 | 0 | 0 | 0 | 1 | 0 | 1 | -720 | 720 | ;

## Defn
xgd_uc Defn
| Matpower # | Matpower Variable Name | Matpower Description | Comments
| 1 | CommitKey | 0 or 1, UC status to use for non-UC runs
| 2 | CommitSched | active power dispatch at time t = 0
| 3 | MinUp | active power dispatch at time t = nt + 1 (only included if explicitly speci ed)
| 4 | MinDown
| 5 | PositiveActiveReservePrice
| 6 | PositiveActiveReserveQuantity
| 7 | NegativeActiveReservePrice
| 8 | NegativeActiveReserveQuantity
| 9 | PositiveActiveDeltaPrice
| 10 | NegativeActiveDeltaPrice
| 11 | PositiveLoadFollowReservePrice
| 12 | PositiveLoadFollowReserveQuantity
| 13 | NegativeLoadFollowReservePrice
| 14 | NegativeLoadFollowReserveQuantity
mpc.gen Defn
| Matpower # | Matpower Variable Name | Matpower Description | Comments | PST # | PST Description
| 1 | GEN_BUS | bus number |  | 1 | number
| 2 | PG | Pg, real power output (MW) |  | 4 | p_gen(pu)
| 3 | QG | Qg, reactive power output (MVAr) |  | 5 | q_gen(pu),
| 4 | QMAX | Qmax, maximum reactive power output (MVAr) |  | 11 | q_gen_max(pu)
| 5 | QMIN | Qmin, minimum reactive power output (MVAr) |  | 12 | q_gen_min(pu)
| 6 | VG | Vg, voltage magnitude setpoint (p.u.) | Set to 1
| 7 | MBASE | mBase, total MVA base of machine, defaults to baseMVA | Pick MVA & mutiply basev
| 8 | GEN_STATUS | status, > 0 - in service, <= 0 - out of service | Set to 1
| 9 | PMAX | Pmax, maximum real power output (MW) | DMNC
| 10 | PMIN | Pmin, minimum real power output (MW) | Mingen
| 11 | PC1 | Pc1, lower real power output of PQ capability curve (MW) | D-curve
| 12 | PC2 | Pc2, upper real power output of PQ capability curve (MW) | D-curve
| 13 | QC1MIN | Qc1min, minimum reactive power output at Pc1 (MVAr) | D-curve
| 14 | QC1MAX | Qc1max, maximum reactive power output at Pc1 (MVAr) | D-curve
| 15 | QC2MIN | Qc2min, minimum reactive power output at Pc2 (MVAr) | D-curve
| 16 | QC2MAX | Qc2max, maximum reactive power output at Pc2 (MVAr) | D-curve
| 17 | RAMP_AGC | ramp rate for load following/AGC (MW/min) | Regulation Ramp Rate
| 18 | RAMP_10 | ramp rate for 10 minute reserves (MW) | 10 spin RR
| 19 | RAMP_30 | ramp rate for 30 minute reserves (MW) | 30 min RR
| 20 | RAMP_Q | ramp rate for reactive power (2 sec timescale) (MVAr/min) | Q Ramp Rate
| 21 | APF | area participation factor | Set to zero
Gencost Defn
| Matpower # | Matpower Variable Name | Matpower Description | Comments
| 1 | Model | cost model, 1 = piecewise linear, 2 = polynomial
| 2 | Startup | startup cost in dollars
| 3 | shutdown | shutdown cost in dollars
| 4 | ncost | number of cost coefficiencts for poly cost fxn, or number of data points for piecewise linear
| 5 | cost | parameters defining total cost function begin here.
mpc.bus Defn
| Matpower # | Matpower Variable Name | Matpower Description | Comments | PST # | PST Description
| 1 | BUS_I | bus number (positive integer) |  | 1 | number
| 2 | BUS_TYPE | bus type (1 = PQ, 2 = PV, 3 = ref, 4 = isolated) |  | 10 | bus_type (1=swing, 2= gen, 3 = load)
| 3 | PD | Pd, real power demand (MW) |  | 6 | p_load(pu)
| 4 | QD | Qd, reactive power demand (MVAr) |  | 7 | q_load(pu)
| 5 | GS | Gs, shunt conductance (MW demanded at V = 1.0 p.u.) |  | 8 | G shunt(pu)
| 6 | BS | Bs, shunt susceptance (MVAr injected at V = 1.0 p.u.) |  | 9 | B shunt(pu)
| 7 | BUS_AREA | area number, (positive integer) | Always set to 1
| 8 | VM | Vm, voltage magnitude (p.u.) |  | 2 | voltage magnitude(pu)
| 9 | VA | Va, voltage angle (degrees) |  | 3 | voltage angle(degree)
| 10 | BASE_KV | baseKV, base voltage (kV) | Pick a kV and change base
| 11 | ZONE | zone, loss zone (positive integer) | Always set to 1
| 12 | VMAX | maxVm, maximum voltage magnitude (p.u.) | Set to 1.1
| 13 | VMIN | minVm, minimum voltage magnitude (p.u.) | Set to 0.9
mpc.branch
| Matpower # | Matpower Variable Name | Matpower Description | Comments | PST # | PST Description
| 1 | F_BUS | f, from bus number |  | 1 | from bus,
| 2 | T_BUS | t, to bus number |  | 2 | to bus,
| 3 | BR_R | r, resistance (p.u.) |  | 3 | resistance(pu),
| 4 | BR_X | x, reactance (p.u.) |  | 4 | reactance(pu),
| 5 | BR_B | b, total line charging susceptance (p.u.) |  | 5 | line charging(pu),
| 6 | RATE_A | rateA, MVA rating A (long term rating) | LTE Rating
| 7 | RATE_B | rateB, MVA rating B (short term rating) | STE Rating
| 8 | RATE_C | rateC, MVA rating C (emergency rating) | Emergency Rating
| 9 | TAP | ratio, transformer off nominal turns ratio |  | 6 | tap ratio,
| 10 | SHIFT | angle, transformer phase shift angle (degrees) |  | 7 | phase shift(deg)
| 11 | BR_STATUS | initial branch status, 1 - in service, 0 - out of service | Set to 1
| 12 | ANGMIN | minimum angle difference, angle(Vf) - angle(Vt) (degrees) | Set to -360
| 13 | ANGMAX | maximum angle difference, angle(Vf) - angle(Vt) (degrees) | Set to 360